# Requirements

_____ pcs of turnkey submersible non-clogging wastewater pump(s). Each pump comes with a _____kW (_____ hp) submersible electric 3-phase motor prepared for operation at _____ volts in 60 Hz complete with _____ feet’s of submersible ATON rubber cable(EPDM-based). The cable shall be sized to match the electrical consumption of the motor running at full load and dimensioned according ICEA and NEMA standards.

The discharge of the pump shall be _____ inch discharge connection and the pump shall be capable of delivering _____GPM at _____ ft TDH. The head at zero flow (shut off head) shall be _____ ft minimum.  On the same curve shall be an additional point at ____ GPM and ____ feet total head.

## Pump design for dry pit installation

The pump shall be capable of continuous non submerged operation in horizontal (Type H) or vertical (Type D) (select one) position installed in a dry pit installation and connected permanently to inlet and outlet pipes. If the pit is flooded, the pump must be capable of operating satisfactory thus being of submersible construction. The motor shall be equipped with a cooling jacket. The cooling liquid shall be led into the cooling jacket via a cylindrical (labyrinth) cutting clearance behind the impeller preventing any solids to enter the cooling jacket.

As to maintain initial peak pump efficiency throughout the life span of the pump, the impeller clearance must be externally adjustable without the need to dismantle the pump. Pump impeller clearance adjustment shall be carried out in such a way that pipes and base plates are not subject to any tensions or mechanical stress when the pumps are operating.

## Pump design for wet pit installation

Each pump shall have a guide claw attached to the pump discharge flange. A replaceable neoprene seal shall be provided as an integral part of the guide claw to form a seal with the base plate. Metal to metal contact surfaces at pump discharge are not acceptable. The guide claw shall direct the pump down by two vertical guide rails to the discharge connection in a simple linear movement without tilting the pump side wards. No portion of the pump shall be supported directly on the bottom of the wet well, guide rails or lifting chain. A cast iron or fabricated steel base plate with integral guide rail holders shall be provided. The base plate shall be designed with an integral 90° elbow, or adapt to a commercially available elbow.

For each pump, _____ feet’s of lifting chain shall be included. The lifting chain must be dimensioned with a  2:1 safety factor.

## Pump construction

The pump casing shall be of cast iron. Pump casing shall be easily removable from the motor for full inspection of impeller.

Pump free passage for solids and impurities shall not be less than 3 inch spherical.

The impeller shall be of SuperVortex design for flows up to 320 GPM or of semi-axial centrifugal flow design, with one to four sweeping vanes and wide flow channels for larger flows. Impeller material shall be cast iron or ductile iron, and Vortex impellers shall be statically balanced whereas channel impellers should be both statically and dynamically balanced. The suction clearance between impeller and pump casing in channel pumps shall be in the axial direction only. The clearance must be fully adjustable with external adjusting screws. To ensure high efficiency over time and low overall operational and running costs, pumps equipped with wear rings are not acceptable.

Other major pump components shall be of cast iron. All exposed fasteners and lock washers shall be of stainless steel.

## Pump motor

The motor shall be watertight according to IEC class IP 68 NEMA MG1 Part 31, and incorporate Class H  Inverter duty rated insulation materials rated for 356°F (180 °C) , with temperature rise class F (221°F (105 °C).

The pump and motor shall be able to operate continuously submerged and capable of handling liquids with a maximum temperature of 104 °F (40°C). Motor housing shall be of cast iron. The rotor shall be solid cast and dynamically balanced. Shaft ends shall be conical for safe securing of impeller. The pump shaft shall be of stainless steel or high-tensile steel in which case the shaft shall be fully protected against contact with the pumped liquid. Shaft bearings shall be open or shielded design greased for life.

Double mechanical shaft seals shall be provided.

The seals shall be oil-lubricated and the seal springs shall be operating in the oil fully protected against contact with the pumped liquid. The seals shall allow for rotation in either direction. The seal area design shall prevent air pocket formation around the seal. All static seals at watertight joints shall be of nitrile O-ring type. Power and control cables shall be clamped against tensile loads and have a serviceable inlet to the motor sealed by compressed rubber ring elements. The pump and electric cables shall be capable of continuous submergence without loss of waterproof integrity to a depth of 65 ft (20 m). The motor shall have internal protection devices consisting of thermo switches embedded in the stator windings, one per phase and a mechanically activated moisture-sensing micro switch without auto-recovery.

The service factor shall be a minimum of 1.10.  The service factor shall be 1.15 A voltage tolerance of plus or minus 10% shall be allowed for the motor. Operation up to 104°F (40°F) ambient and with a temperature rise not to exceed 221°F shall be acceptable for the motor.

If requested, a motor performance chart can be provided.

Design of power cable shall be according to NEMA Standards. The length of the power cable shall be sufficient in order to reach the junction box without the needs to splice it with another cable.

The power provided by the motor shall be adequate e.g. providing enough power to ensure that pump is not overloading throughout the pump performance curve from 0 to max flow.

## Control cable

The control cable must be designed for use with submersible pumps and shall be capable of continuous submergence without loss of waterproof integrity to a depth of 65 ft (20 m). The cable shall allow a maximum conductor temperature off + 194 °F (90°C) and a minimum ambient temperature off - 58°F (- 50°C). The conductor shall be stranded plain copper conductor class 5 according IEC 60228.

## Bearings

Motor bearings are greased for life.

The upper support bearing shall be single row deep-groove bearing.

The lower bearing shall be double row angular contact ball bearing or two pair mounted single row angular contact ball bearings in motors up to 59kW/1800 rpm. Whereas angular contact ball bearing (single or pair mounted) and roller bearing arrangement shall be used in motors starting 73kW/1800rpm, 110kW/1200rpm and 32kW/900rpm.

Bearings shall be designed for a nominal L10 life time of 25000 hr to and below 152 kW and 50000hr above 152 kW at best efficiency point.

## Shaft seals

The pump shall have a primary and secondary shaft seal allowing for rotation in either direction.

The material combination of the primary shaft seal of all pump types shall be silicon carbide/silicon carbide. For the secondary shaft seal, the material combination shall be silicon carbide/carbon.

Sealing between the slip rings shall be based on extremely smooth and flat contact surfaces of the slip rings. The surfaces shall be in such close contact that no or only a very minute leakage can pass between them. The flatness and smoothness of the rings shall be in the magnitude of 0,0005 mm and the faces shall be finished by lapping. The slip rings shall seal against the stationary seat or shaft with O-rings.

The shaft seals shall be placed in the oil chamber of the pump. The oil chamber shall provide a reliable sealing between the pumped liquid and the motor.

The shaft seals shall have no springs or other parts in direct contact with the pumped liquid. The shaft seals shall be bidirectional, meaning that they can operate in either direction thus allowing for back-flow of liquid through the pump.

## Impeller (for SV pumps(Super Vortex impeller))

The impeller shall be of cast iron 80-55-06 according ASTM A536-84, designed as symmetrical multi vane winglets impeller capable of running against closed valve. The design must ensure flow entirely outside the impeller providing limited contact between the impeller and the pumped liquid and ensure that long fibers, rags with more passes freely through the pump without getting caught and without causing clogging or jamming.

## Impellers (for S pumps (channel impeller)

The impeller shall be of cast iron 80-55-06 according ASTM A536-84,, in single, double, triple or quad channel design, statically and dynamically balanced of semi-axial centrifugal flow design with long, self-cleaning and none clogging vane(s).

The suction clearance between impeller and pump casing in channel pumps shall be in axial direction only. The clearance shall be fully adjustable with external adjusting screws. To ensure high efficiency over time and low overall operational and running costs, pumps equipped with wear rings are not acceptable.

Impeller(s) shall be keyed to the shaft and have an impeller bolt for locking the impeller to the shaft. In case of shaft not being stainless steel, a stainless steel impeller cap with an O-ring shall protect the shaft end from the pumped media. The impeller shall be capable of passing a minimum _____ inch diameter solid.

## Volute

The volute shall be cast iron Class 35B (ASTM A48) or cast iron 80-55-06 (ASTM A536-84).

The volute must be in non-concentric design with smooth passages large enough to pass any solids that may enter the impeller. The inlet and discharge size shall be as according to requirements.

## Protection

The stator shall have three thermal protectors (thermal switches or thermistors, one per each phase) and one or two moisture switches (placed in the terminal box and stator housing. The thermal and moisture protectors shall be connected in separate circuits.

The motor shall as option have the possibility to install water in oil analogue sensor in the oil chamber for continuous monitoring of shaft seal condition.

Furthermore the motor(s) shall allow for installation of sensors for measurement of temperatures in bearings and windings and installation of vibration senor for motors above 30 kW for condition monitoring.

All monitoring sensors shall be connected to the Grundfos IO 111 sensor module which can be integrated to the control system and communicate with PLC controls and communication package via 4-20 mA signals.

97910507 0311